## 1.Dismant&reloc
Reorganization of ECM
1 | Dismantling and relocation works
| Works Description | Unit | Quantity | Unit price | Total price
1.1 | Dismantling of Building R (former Cafeteria). One story building consisting of 20'office containers,10' of ablution units combined with steel structure. All 20'/10' containers are to be transported to EPC Prishtina / TEC Dumosh to a site designated by EULEX Project Manager. Debris is to be removed from site. 130m2 gross area. See technical specifications and dwg for more details. | LS | 1 |  | 0
1.2 | Dismantling of Block 6 - one story office building consisting of 20' office containers and 20'/10' ablution units. All 20' containers are to be transported to EPC Prishtina / TEC Dumosh. 10' containers (3pcs) are to be relocated within the ECM compound to a site designated by EULEX Project Manager. Debris is to be removed to a designated dump site. See technical specifications and dwg for more details. 316m2 gross area | LS | 1 |  | 0
1.3 | Dismantling of Block 7 - G+1, two story office building consisting of 20' office containers and 20' ablution units combined with steel structure. 15 office +2 Ablution unit of 20' containers are to relocated within the ECM compound to a site designated by EULEX Project Manager, all other containers are to be transported to EPC Prishtina / TEC Dumosh. Debris is to be removed from site. See technical specifications and dwg for more details. 740m2 gross | LS | 1 |  | 0
1.4 | Dismantling of Block5 - one story security building consisting of two (2) 20' office containers and relocated within the compound to a site designated by EULEX Project Manager. Debris is to be removed to a designated dump site. See technical specifications and dwg for more details. 28m2 gross area | LS | 1 |  | 0
1.5 | Dismantling of Block K, one story building consisting of 3 office containers and relocated the same within the compound to a site designated by EULEX Project for further use(see BoQ. #3) | LS | 1 |  | 0
1.6 | Dismantling of soak pit platform consisting of metal sheets platform, wooden platform and metal structure, area 116m2 Price to include removal of the platform stairs as well. Metal sheets to be handed over to EULEX. Steel structure to be taken off from the Compound. | LS | 1 |  | 0
1.7 | Dismantling of parking roof cover 77m2 beside block 8 and installing of the same in line fence with UNMIK in continued line with existing parking covers. Prior installation the 6 (six)pcs of concrete cube foundation 60x60x60 cm to be constructed with on top steel plate 300x300x10mm anchored on concrete. Welding works and painting of the structure with primary and final oil paint, to be included in the price. Dim 15x5m. | EA | 1 |  | 0
1.8 | Dismantling part of the parking cover attached to the Helipad T Walls as per drawing provided #02 , cut for ~1m (roof cover, truss and columns). Relocate two (2) cut columns for 1 m', prior the 2(two)pcs of concrete cube foundation 60x60x60 cm for poles to be constructed with on top steel plate 300x300x10mm anchored on concrete. Welding works and painting of the welding parts, to be included in the price | LS | 1 |  | 0
1.9 | Dismantling of the underground PE septic tank capacity 3000 l, located nearby cafeteria, area to be cleaned , debris to be sent out of the compound. | LS | 1 |  | 0
1.1 | Dismantling and removal of three 500l water tanks within the compound with reconnection to the water system with all necessary fittings, piping and Pumps. Pumps are existing one, they are to be disconected first and then reinstalled in the Ablution unit of the new blocks ( SSD, FPU and Ablution for BI). | ea | 3 |  | 0
|  |  |  | Total | 0

## 2.Entrance modification
Reorganization of ECM
2 | Modification of ECM Main Entrance
| Works Description | Unit | Quantity | Unit price | Total price
Dismantling/demolition/adjustment works
2.1 | Dismantling of the 3m high fence together with polycarbonate cover in existing pedestrian entry, save on side for further use. | m' | 28.37 |  | 0
2.2 | Demolition of the concrete foundation of the dismantled fence, up to the land level, debris to be taken off from the site | m3 | 3 |  | 0
2.3 | Demolition half of wall together with concertina wire in right side of entrance in high 110wall+60cm along with concertina wire (part above the middle beam, see dwg #04 & #26 provided) and creating of two openings for pedestrian gates of 100cm width in the same wall. Debris to be transported out of the compound. | m' | 25.5 |  | 0
2.4 | Demolition of the wall marked in dwg#4, were the waste is placed, wall is made from concrete blocks reinforced with concrete beams and columns( see dwg #27) debris to be taken off from the site | m' | 11.8 |  | 0
2.5 | Demolition of the concrete wall in left side in entry cage with Dim 300 x 126 x. 30cm. Debris to be taken off from the site | Ea | 1 |  | 0
2.6 | Demolition of the wall in fuel station , made from concrete blocks reinforced with concrete beams an columns. Debris to be taken off from the site, end of remain wall to be reinforced with reinforcement concrete column 20x20cm in cube reinforcement foundation 60x60x60cm.(see photo in technical description) | m' | 4 |  | 0
2.7 | Dismantle the existing entry metal gate of fuel station, save on side and reinstall after adjustment of the entry with all necessary fittings, painting, welding, new concrete foundations 60x60x60cm for two side columns, dim. 820x220 (see photo in technical description) | EA | 1 |  | 0
2.8 | For road widening, removal of 5 five T walls in fuel station with dim 1.5x3m in distance ~4 m ( see dwg #2 & #4) | EA | 5 |  | 0
2.9 | Dismantle of existing vehicle entry gate with Dim 765x300cm, adjust for new reduced opening ~650 cm(cut in both sides from the middle ~50+50cm) and reinstall with all needed weldings, cuttings, paintings, new columns 100x100x4mm, with construction of the new cube concrete foundation 60x60x60cm. | EA | 1 |  | 0
2.1 | Dismantle be folding metal gate in waste area and reinstall in new set area for waste, constructing the two cube concrete foundations 60x60x60cm with anchored metal plate 300x300x10mm on it. Gate Dim. 600x200 cm | EA | 1 |  | 0
2.11 | Dismantle the second boom gate of entry together with head column profiles, rotate and reinstall in existing steel I profiles with all necessary welding's and paintings for proper functionality of the boom gate. | EA | 1 |  | 0
2.12 | Demolish concrete cubes of the first entry boom gate up to asphalt level. The upper surface to be nicely leveled with the existing road. | EA | 2 |  | 0
2.13 | Provide material and construction of the new concrete foundations with C25/30, with reinforcement mesh in the bottom ᴓ12mm/10cm. Foundation to be placed in 10cm of compacted gravel 0-30mm. Dim 80x80x70+10cm gravel | EA | 2 |  | 0
2.14 | Provide with material and install columns made from new ] steel profiles as per dwg #25, in the concrete foundations from previous item. Profiles are to be welded, treated with antirust paint2x and with final oil paint as per site engineer instructions. | EA | 2 |  | 0
2.15 | Dismantle, rotate and install the first boom gate of entrance together with head column profiles, rotate and reinstall in new constructed columns from previous item, with all necessary weldings and paintings for proper functionality of the boom gate. | EA | 1 |  | 0
2.16 | Dismantle existing entry pedestrian door (first one) with fence dim.580 x300cm, adjust as per new opening dim~ 315 x300cm and reinstall with all needed weldings, cuttings, paintings, new columns with cube concrete foundation 60/60x60with were steel plate 30x30x1cm is to be anchored. | LS | 1 |  | 0
2.17 | Dismantle existing entry pedestrian door (second one) with fence dim.356 x300cm, adjust as per new opening dim~ 140x300cm and reinstall with all needed weldings, cuttings, paintings, new columns with cube concrete foundation 60/60x60cm were steel plate 30x30x1cm is to be anchored. | LS | 1 |  | 0
2.18 | Dismantle the 2(two) existing pedestrian door 100x200cm together with fence and reinstall the same in the openings created in the wall from item1.3. with all needed weldings, cuttings, paintings, anchoring.. | Ea | 2 |  | 0
Asphalt/pavement works
2.19 | Mechanical excavation of soil with transportation to the local dump site. Excavations carried out and leveled as to the given project and given elevations. The sides of the excavation to be properly cut and the bottom to be properly leveled. | m3 | 20 |  | 0
2.2 | Supply, transport, spreading in layers, compaction and fine planning of gravel. Gravel is to be fill in the predicted layer and compacted until the required density:
| 0-31.5mm in thickness of 20cm | m3 | 15 |  | 0
| 31.5 -60mm in thickness of 30cm | m3 | 7.5 |  | 0
2.21 | Provide material and laying of asphalt layer mixture AB 16 , t- 6cm, including compaction, prior cleaning the surface prepared for asphalting (existing macadam, asphalt, concrete roadway or gravel) and spreading bitumen emulsion min. 0.8 kg/m2 | m2 | 280 |  | 0
2.22 | Supply and paving with rectangular concrete paving tiles. Tiles are to be placed in a layer of compacted gravel 0-30mm, t-20cm and sand d=3~5cm, including excavation works. Price to include all layers. Tiles dim. 10x20x6 cm | m2 | 110 |  | 0
2.23 | Supply and installation of concrete kerbs. Kerbs to be installed in the cement mortar with proportions l: 2. Grout lines to be grouted and gently retract against the curb. Price per m' of kerbs.
| section 20/8 cm -for paving tiles | m' | 42 |  | 0
| section 24/18-12 cm -for asphalt area | m' | 22 |  | 0
2.24 | Provide with material and construction of the concrete stairs in entry and exit of the reception pedestrian entry including excavation and form works. Dim. 190x60(30+30) x h 30(15+15) cm | EA | 2 |  | 0
|  |  |  | Total | 0

## 3. SSD Blocks
Reorganization of ECM
3 | SSD Block
| Works Description | Unit | Quantity | Unit price | Total price
Ground Works
3.1 | Cutting of asphalt and excavating of strip foundation trenches for office containers as per the designs provided. Note and include in the price that under 20-30cm of the land level, exist underground reforcement concrete slab thicknes 20-30cm that is to be broken, to create required depth of the strip foundation (dwg #10) | LS | 1 |  | 0
3.2 | Providing with material, filling and compaction of strip foundations with gravel 0-31mm, thickness 10cm. Prior graveling, the soil under the gravel should be compacted as well. | m3 | 5.5 |  | 0
3.3 | Backfilling of soil/gravel around the foundations strip after construction of foundation, and removal of surplus material from site. | LS | 1 |  | 0
3.4 | Supply and installation of concrete kerbs around the reception block, 40cm from the object in all sides, including excavation and refiling works. Kerbs to be installed in the cement mortar with proportions l: 2. Grout lines to be grouted and gently retract against the curb. Price per m' of kerbs.Dim 20/8 cm | m' | 48 |  | 0
3.5 | Provide and laying of the river stones around foundations in width of 40cm in thickness 10cm, in a straight line | m2 | 18 |  | 0
Reinforcement and Concrete Works
3.6 | Provision of materials and installation of reinforcement as per specifications/drawings provided ( using bars of Ø10 mm, Ø12 mm and Ø8mm) | kg | 548.6 |  | 0
3.7 | Provision of material and concreting of the reinforced strip foundation with concrete C-25/30, including formwork as required. Note: concrete quality lab tests are to be conducted for the used concrete ( cubes 150x150x150mm >28days) | m3 | 7.4 |  | 0
Grounding Protection
3.8 | Provide material and install grounding protection. Grounding is to be provided in the horizontal reinforcement of the foundation with FeZn strips of size 40x4mm throughout the perimeter, with 1 meter strip extensions in two corners, price to include crosswise elements with related fittings and Zn Rod of 1.5m'. | LS | 1 |  | 0
Construction works
3.9 | Rearrangement of office containers' wall - short side, relocating the panels (dismantling&reinstalling) as and where required by replacing the damaged panels/window panels/door panels, as per bld layouts dwg #09 and technical specifications. Panels required will be used from dismantled containers. Short side wall of the container consists of two panels. Price to include dismantling and reinstallation of any skirting as part of the short side wall as well. | EA | 4 |  | 0
3.1 | Dismantling of office containers' wall - long side, as and if required by creating double rooms as per bld layouts dwg 09. Long side wall consists of 5 panels. Price to include dismantling any skirting as part of the wall as well. | EA | 6 |  | 0
3.11 | Installation of office containers' wall - long side, as and if required by creating single, double rooms as per bld layouts . Panels required will be used from dismantled containers. Long side wall consists of 5 panels. Price to include reinstallation of any skirting as part of the wall as well. | EA | 6 |  | 0
3.12 | Dismantling/demolition works in the shower/ablution unit. All the sanitary equipments, installations and existing partitions are to be dismantled/demolished. sanitary equipment to be save on site for later reuse. Debris to be transported to the city dump site. Prior to transportation clearance for the items to be taken from the EULEX Representative. | EA | 4 |  | 0
3.13 | Demolition of the damaged floor layers for office containers and ablution unit (linoleum +plywood+steam blockade + insulation). Price should include transportation of debris to the city dump site. Note: Only if the floor panels are damaged. Each container is to be assessed jointly with EULEX Engineer during construction. | m2 | 126 |  | 0
3.14 | Provide material and place 100mm mineral wool insulation throughout the office containers floors, ablution unit and above the containers between the trusses. | m2 | 126 |  | 0
3.15 | Provide material and install plastic sheet 0.2mm all over the office and ablution flooring. | m2 | 126 |  | 0
3.16 | Provide material and install 20mm thick plywood flooring throughout the office containers and first floor corridor surface. | m2 | 112 |  | 0
3.17 | Provide and install 20mm thick water-resistant plywood flooring for the ablution units. | m2 | 14 |  | 0
3.18 | Provide material and install final coat flexible PVC,through the floor of the office containers t=2mm, including flooring of the refurbished ablution units where the pvc is to be 15 cm height up to the wall. PVC is to be welded & glued with proper adhesive. Skirtings all around the perimeter of the surface is to be included in the price. Color to be chosen by EULEX Representative. PVC 2.0mm thick, commercial use, EN 649, classification as per EN 685 Class 33, areas with heavy traffic. | m2 | 130 |  | 0
3.19 | Provide and install external PVC double wing door. The main entrance door should be of PVC profiles as per design provided (dwg # 15) DIM 150/230cm Glass: double, fully insulated, thermal protection, 6+12+4mm. Door is to be equipped with door lock complete, minimum three keys. | EA | 2 |  | 0
3.2 | Provide and install metal solid door as emergency exit door, equipped with anti panic push bar, pneumatic door closer, and possibility to close with a key from outside. Measurements to be taken on the spot. dim 95/210cm | EA | 1 |  | 0
3.21 | Provide and install office PVC Window dim 95x125cm, as per design provided. Glass: double, fully insulated, thermal protection, 6+12+4mm (dwg #15), prior the container panel to be cut /old window to be dismantled. | EA | 13 |  | 0
3.22 | Provide and install toilet PVC Window dim 60x80cm, as per design provided. Glass: double, fully insulated, thermal protection, 6+12+4mm (dwg 15 )prior the container panel to be cut | EA | 1 |  | 0
3.23 | Provide material and construct roof metal structure, consisting of trusses with profiles 60X40X3mm and 40x2.5mm including purlins 60X40X3mm as per design provided, dwg 11. In total 5 trusses are required . | Kg | 1469 |  | 0
3.24 | Provide and install pre-painted corrugated metal sheet of t=0.55mm as roof cover with drip stop layer. Price to include snow guards and roofing ridge cap which is to cover min. 30cm in both sides. Color RAL 9002. Slope surface calculated. | m2 | 141 |  | 0
3.25 | Provide and install pre-painted (piano) metal sheet roof eaves 50 cm overhang, of 0.50mm thickness. Color RAL 9002 (fascia and soffit all sides). | m2 | 22 |  | 0
3.26 | Provide and install half round horizontal rain gutters 150mm, from pre-painted metal sheet 0.6mm thickness. Color RAL9002. Price shall include as well provision and installation of hangers and all the required accessories. | m' | 22 |  | 0
3.27 | Provide and install vertical gutters ( Rainwater down pipes 100mm diameter), of pre-painted metal sheet 0.6mm thickness. Color RAL 9002. | m' | 12 |  | 0
3.28 | Provide and install pre-painted metal sheet roof edges/A sides 0.50mm thickness (piano). Color RAL 9002. Price shall include the required flushings where the two different height roofs meet and the roof ventilation grill. | m2 | 28 |  | 0
3.29 | Provide material and seal the joints between containers for the double container rooms (walls/ceiling). Sealing is to be done with pre-painted flat metal sheet thickness 0.60mm. Prior to installation the gaps between two containers are to be filled with foam/mineral wool as required. Color similar to interior paint. | m' | 35 |  | 0
3.3 | Provide and install galvanized metal sheet strip 41cm wide t=2mm for covering the floor joints of double office containers. Prior to installation the gaps between two containers are to be filled with mineral wool as required | m' | 18 |  | 0
3.31 | Provide and install 10cm mineral wool above all containers, between steel trusses | m2 | 118 |  | 0
3.32 | Provide and install plastic sheet 0.2mm through the ceiling above the mineral wool. | m2 | 125 |  | 0
3.33 | Provide material and paint interior of all office/ablution unit, including corridor with acrylic enamel paint 2x. Paint characteristics: semi-gloss coating, eco-friendly, without unpleasant odor, thinning with water. Paint is to be applied by spraying. Previously the surface is to be cleaned of dust and any debris. | m2 | 362 |  | 0
3.34 | provide with material and concreting of stairs at the entrance of the building with C-25/30 concrete, including frame works Dim 160x60(30+30) x h 32(16+16) cm | Ea | 1 |  | 0
3.35 | Provision and installation of room numbers | EA | 10 |  | 0
3.36 | Dismantling of existing AC window unit in all containers which is to be delivered to EULEX representative. After disassembly, the remaining gap with dim. 80 x 65cm is to be closed from inside and outside with 0.6 mm prepainted metal sheet with sufficient overlap and in the middle filled with styrodur t-60mm. | EA | 7 |  | 0
3.37 | Supply and install split unit Air Conditioner 12000 BTU, quality as per technical specifications. In the price to be calculated drilling of necessary holes, piping, wiring and brackets for AC . Note: due to the facade to be installed over the container panels the brackets to be provided for the outside unit are to be longer. | EA | 5 |  | 0
3.38 | Provide and replace all door cylinders (offices and ablution unit). New cylinders should have minimum three keys, adjusting also the existing door lock. | EA | 5 |  | 0
20' Ablution Unit
3.39 | Provide and install toilet partitions as per dwg provided. Toilet partitions/door are to be waterproof compacted panels with thickness -12mm. Compacted panel are to be impact and scratch resistant, waterproof, easy to clean, bacteria resistant, color white, finish – mat. Partition walls that divides the F/M ablution and the walls that divided showers are to be of full height floor/ceiling. Walls and doors at the toilet area are to be pedestal mounted and ceiling braced, doors dim. 70cm*195 furnished with a toilet lock (free/occupied). Pedestal type stainless steel legs. Profiles to be used are to be square clear anodized aluminum profiles, resists to corrosion, mold and fungus. Urinal partitions are to be of the same material as well. | m2 | 22 |  | 0
3.4 | Install dismantled boiler of 200l - item 3.10 ( boiler is to have three polar separate circuit breaker) | EA | 1 |  | 0
3.41 | Install dismantled toilets complete with flushing tank and built-in bidet tube. All water closets for toilets as shown on the drawings shall be dual function flush tank with built-in bidet tube, white, with complete fittings and mounting accessories | EA | 3 |  | 0
3.42 | Install dismantled shower basis. Modifications on the height (bolts) of the shower basis are required in order to fit the sewerage pipes underneath. Price to include reinstallation of dismantled shower heads and flexible hose (wall hanged as well), water tap and pvc curtains with inox tube. | EA | 3 |  | 0
3.43 | Provide and install new washbasin with faucet complete with faucet, standard fittings, trap and lavatory brackets and other accessories | EA | 3 |  | 0
3.44 | Install dismantled urinals complete with faucets. | EA | 1 |  | 0
3.45 | Install dismantled mirrors over each washbasin | EA | 3 |  | 0
3.46 | Design and built water supply network& sewerage system with connections to the existing network. Price per ablution and kitchen (kitchen-1(one) washing base) | EA | 1 |  | 0
Facade works
3.47 | Remove existing metal holders connecting two containers, welding of the containers in between. Removed metal holders to be handed over to EULEX | LS | 1 |  | 0
3.48 | Provide materials and install lightweight façade made of expanded polystyrene plates 100mm thick ( over panels 80%) and 50mm(over columns 20%), with all necessary elements and layers including render finish and final paint, as per technical specification according to DIN EN 13501 | m2 | 143 |  | 0
3.49 | Provide and install window sills of prepainted metal sheet 1mm. | m' | 14 |  | 0
3.5 | Provision and installation of scaffolding during the works including screen to secure particles/dust from spreading outside the working area. | LS | 1 |  | 0
Electrical Works
3.51 | Dismantling of the existing electrical/IT installations within the provided EULEX office containers. All the materials dismantled ( switches, lights, plugs) are to be handed over to EULEX Representative. Individual containers electrical panels are to not be dismantled, but to remain and be reused. Clearance for any removal of debris from the site is to be taken from the Project Manager of EULEX. | EA | 8 |  | 0
3.52 | Install main electrical panel for the building, complete with main switch AS 80A, circuit breaker 2x 32A tree poles and two(2) circuit breaker 16A. Price to include grounding of the panel with the material required. | EA | 1 |  | 0
3.53 | Provide material and install containers electrical connections (maximum 4 containers on a line), for the whole containerized building. Connections are to be done with cabling flexible 5x6mm2, directly in the fuse box inside the container. Prior the industrial plugs of 32 A are to be removed. | EA | 8 |  | 0
3.54 | Connection of containers in between with cable 1x35mm2 for earthling. | LS | 1 |  | 0
3.55 | Provide and install LED Flood light reflector 100W with all necessary cabling 3x1.5mm and dark censor of 10A. Installation to be done in entry part of roof A form, in galvanized metal poles fixed on the structure of the containers. Price to include circuit breakers, cabling, dark sensor, and other fittings as required. | EA | 1 |  | 0
3.56 | Provide and install single phase double socket outlets, wall/panel mounted, 16A, 220V. Price is to include the - Cable type PPY 3x2,5mm² and all the required fittings for functional sockets. Cables are to be covered with proper PVC trunkings. | EA | 19 |  | 0
3.57 | Provide and install single phase single sockets for AC's, complete with required fittings 16A, 220V. Price is to include all the cabling provision and installation PPY 3x2,5mm², with the required fittings. Cables to be covered with PVC trunking. | EA | 4 |  | 0
3.58 | Provide and install single phase single sockets suitable for toilets/IP65/with cover, complete with required fittings 16A, 220V. Price is to include all the cabling provision and installation PPY 3x2,5mm², with the required fittings. Cables to be covered with PVC trunking. | EA | 1 |  | 0
3.59 | Provide and install surface mounted LED lights, 1x40W (dim 30x120cm). Price is to include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC trunking. | EA | 14 |  | 0
3.6 | Provide and install surface mounted slim LED lights 40w within ablution units, IP65 Price shall include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC trunking. | Ea | 3 |  | 0
3.61 | Provide and install surface mounted LED lights for F toilet, IP65, water resistant, 1x18W. Price shall include also provision and installation of the required cabling for functional lights - cable type PPY3x1.5mm2. Cabling is to be covered with proper PVC trunking. | Ea | 1 |  | 0
3.62 | Provide and install halogen light fitting with LED bulb GU10-230 volt.3-5 watt, Ø60mm, surface mounted. Price is to include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC trunking. | EA | 2 |  | 0
3.63 | Provide and install Emergency EXIT LED light 10W as per dwg provided, including cabling and all the trunking required. | EA | 1 |  | 0
3.64 | Provide and install Emergency LED light 10W as per dwg provided, including cabling and all the trunking required. | EA | 1 |  | 0
3.65 | Provide and install light switches 6A (single/double pole, and alternative ) mounted on wall panels with all required cabling/accessories for functional switch. | EA | 4 |  | 0
3.66 | Provide and install moving sensors for ablution units lights 360º, ceiling mounted with all required cabling/accessories for functional sensor. | EA | 5 |  | 0
3.67 | Provide and install electrical panel with 3 poles circuit breaker 32A, with supply cable 5x6mm2 from the main electrical panel, required for the IT Rack Cabinet. | EA | 1 |  | 0
| Heating troupes | Unit | Quantity
3.68 | provide and install Wall Mounted Electrical Heater with Capacity 2000W, including thermostat. | EA | 7 |  | 0
| Kitchen elements | Unit | Quantity
3.69 | Provide and install electrical stove complete with oven and cooktop. Dim~ 60x60x85cm | Ea | 1 |  | 0
3.7 | Provide and install fridge with small freezing part(-) Dim~ 60x60x140cm | EA | 1 |  | 0
3.71 | Provide and install microwave. Dim. ~ 45x25x30cm | EA | 1 |  | 0
3.72 | Provide and install kitchen sink -stainless still with cabinet, complete with proper tap for cold and hot water. Cabinet is to be from plywood, white color. Bench top to be plasticized and waterproof. In the price to be calculated all accessories for sink connection to the existing cold/hot water and sewerage system . Dim 120x60x90 | EA | 1 |  | 0
3.73 | Provide and install kitchen cabinet (working table) from white plywood, with upper working bench top from waterproof plasticized material. Dim 120x60x90 | EA | 1 |  | 0
Reception Block
Ground Works
3.74 | Cutting of asphalt/concrete slab and excavating of strip foundation trenches for office containers as per the designs provided. Note and include in the price that under 20-30cm of land llevel, exist underground reforcement concrete slab thicknes 20-30cm that is to be broken, to create required depth of the strip foundation as per the designs #14 | LS | 1 |  | 0
3.75 | Providing with material, filling and compaction of strip foundations with gravel 0-31mm, thickness 10cm. Prior graveling, the soil under the gravel should be compacted as well. | m3 | 0.8 |  | 0
3.76 | Backfilling of soil/gravel around the foundations strip after construction of foundation, and removal of surplus material from site. | LS | 1 |  | 0
3.77 | Supply and installation of concrete kerbs around the reception block, 40cm drom the object in 3 (three) sides,including excavation and refiling works. Kerbs to be installed in the cement mortar with proportions l: 2. Grout lines to be grouted and gently retract against the curb. Price per m' of kerbs. Dim 20/8 cm | m' | 24 |  | 0
3.78 | Provide and laying of the river stones around foundations in width of 40cm in thickness 10cm, in a straight line | m2 | 9 |  | 0
Reinforcement and Concrete Works
3.79 | Provision of materials and installation of reinforcement as per specifications/drawings provided ( using bars of Ø10 mm, Ø12 mm and Ø8mm) | kg | 316.4 |  | 0
3.8 | Provision of material and concreting of the reinforced strip foundation with concrete C-25/30, including formwork as required. Note: concrete quality lab tests are to be conducted for the used concrete ( cubes 150x150x150mm >28days) | m3 | 4.5 |  | 0
Grounding Protection
3.81 | Provide material and install grounding protection. Grounding is to be provided in the horizontal reinforcement of the foundation with FeZn strips of size 40x4mm throughout the perimeter, with 1 meter strip extensions in two corners, price to include crosswise elements with related fittings and Zn Rod of 1.5m'. | LS | 1 |  | 0
Construction works
3.82 | Rearrangement of the office containers' wall, relocating the panels (dismantling&reinstalling) as a required by replacing the full panels/window panels/door panels, as per bld layouts dwg #14 and technical specifications. Panels required will be used from dismantled containers. Price to include dismantling and reinstallation of any skirting as part of the wall as well. Unit price is per panel dismantled and reinstalled | EA | 9 |  | 0
3.83 | Provide material and construct complete roof which consist of metal structure trusses(total 5 trusses), metal purlins, prepainted metal sheet cover with drip stop layer including ridge cup and snow guards, prepainted metal sheet (piano) for eaves and A-sides and mineral wool with plastic sheet cover between the trusses. See dwg #14 Calculation per M2 of horizontal projection: | m2 | 74 |  | 0
3.84 | Provide and install half round horizontal rain gutters 150mm, from pre-painted metal sheet 0.6mm thickness. Color RAL9002. Price shall include as well provision and installation of hangers and all the required accessories. | m' | 21 |  | 0
3.85 | Provide and install vertical gutters ( Rainwater down pipes 100mm diameter), of pre-painted metal sheet 0.6mm thickness. Color RAL 9002. | m' | 12 |  | 0
3.86 | Provide material and seal the joints between containers for the double container rooms (walls/ceiling). Sealing is to be done with pre-painted flat metal sheet thickness 0.60mm. Prior to installation the gaps between two containers are to be filled with foam/mineral wool as required. Color similar to interior paint. | m' | 12 |  | 0
3.87 | Provide and install galvanized metal sheet strip 41cm wide t=2mm for covering the floor joints of double office containers. Prior to installation the gaps between two containers are to be filled with mineral wool as required | m' | 12 |  | 0
3.88 | Provide material and paint interior of all offices, walls and ceiling, with acrylic enamel paint 2x. Paint characteristics: semi-gloss coating, eco-friendly, without unpleasant odor, thinning with water. Paint is to be applied by spraying. Previously the surface is to be cleaned of dust and any debris. | m2 | 174 |  | 0
3.89 | Provide and install office PVC Window dim 95x125cm, as per design provided. Glass: double, fully insulated, thermal protection, 6+12+4mm (dwg #15), prior the container panel to be cut /old window to be dismantled. | EA | 3 |  | 0
Facade works
3.9 | Remove existing metal holders connecting two containers, welding of the containers in between. Removed metal holders to be handed over to EULEX | LS | 1 |  | 0
3.91 | Provide materials and install lightweight façade made of expanded polystyrene plates 100mm thick ( over panels 80%) and 50mm(over columns 20%), with all necessary elements and layers including render finish and final paint, as per dwg #24 and technical specification according to DIN EN 13501 | m2 | 94 |  | 0
3.92 | Provide and install window sills of prepainted metal sheet 1mm. | m' | 9 |  | 0
3.93 | Provision and installation of scaffolding during the works including screen to secure particles/dust from spreading outside the working area. | LS | 1 |  | 0
Electrical Works
3.94 | Install main electrical panel for the reception, complete with main switch AS 63A and circuit breaker 1x 32A tree poles. Price to include grounding of the panel with the material required. | EA | 1 |  | 0
3.95 | Rearrangement of the electrical switches, plugs as per new set-up with necessary cabling covered with pvc canals. Lights , plugs , switches are to be used the existing ones. | LS | 1 |  | 0
| Heating troupes | Unit | Quantity
3.96 | provide and install Wall Mounted Electrical Heaters with Capacity 2000W, including thermostats. | EA | 4 |  | 0
|  |  |  | Total | 0

## 4. FPUCommanders block
Reorganization of ECM
4 | FPU Commanders block
| Works Description | Unit | Quantity | Unit price | Total price
Ground Works
4.1 | Cutting of asphalt and excavating of strip foundation trenches for office containers as per the designs provided. Note and include in the price that under 20-30cm of the land level, exist underground reforcement concrete slab thicknes 20-30cm that is to be broken, to create required depth of the strip foundation as per the designs(dwg # 18) | LS | 1 |  | 0
4.2 | Providing with material, filling and compaction of strip foundations with gravel 0-31mm, thickness 10cm. Prior graveling, the soil under the gravel should be compacted as well. | m3 | 2.5 |  | 0
4.3 | Backfilling of soil/gravel around the foundations strip after construction of foundation, and removal of surplus material from site. | LS | 1 |  | 0
4.4 | Supply and installation of concrete kerbs around the reception block, 40cm drom the object in all sides, including excavation and refiling works. Kerbs to be installed in the cement mortar with proportions l: 2. Grout lines to be grouted and gently retract against the curb. Price per m' of kerbs. Kerb stone dim 20/8 cm. | m' | 44.7 |  | 0
4.5 | Provide and laying of the river stones around foundations in width of 40cm in thickness 10cm, in a straight line | m2 | 18 |  | 0
Reinforcement and Concrete Works
4.6 | Provision of materials and installation of reinforcement as per specifications/drawings provided ( using bars of Ø10 mm, Ø12 mm and Ø8mm) | kg | 751.4 |  | 0
4.7 | Provision of material and concreting of the reinforced strip foundation with concrete C-25/30, including formwork as required. Note: concrete quality lab tests are to be conducted for the used concrete ( cubes 150x150x150mm >28days) | m3 | 11.5 |  | 0
Grounding Protection
4.8 | Provide material and install grounding protection. Grounding is to be provided in the horizontal reinforcement of the foundation with FeZn strips of size 40x4mm throughout the perimeter, with 1 meter strip extensions in all 4(four) corners, price to include crosswise elements with related fittings and Zn Rod of 1.5m'. | LS | 1 |  | 0
Construction works
4.9 | Rearrangement of office containers' wall - short side, relocating the panels (dismantling&reinstalling) as and where required by replacing the damaged panels/window panels/door panels, as per bld layouts (dwg #16 &#17) and technical specifications. Panels required will be used from dismantled containers. Short side wall of the container consists of two panels. Price to include dismantling and reinstallation of any skirting as part of the short side wall as well. | EA | 10 |  | 0
4.1 | Dismantling of office containers' wall - long side, as and if required by creating double rooms as per bld layouts (dwg #16 & #17). Long side wall consists of 5 panels. Price to include dismantling any skirting as part of the wall as well. | EA | 8 |  | 0
4.11 | Installation of office containers' wall - long side, as and if required by creating single, double rooms as per bld layouts (dwg #16 & #17). Panels required will be provided by EULEX. Long side wall consists of 5 panels. Price to include reinstallation of any skirting as part of the wall as well. | EA | 8 |  | 0
4.12 | Dismantling/demolition works in one 10'ablution unit. All the sanitary equipments, installations are to be dismantled/demolished. Sanitary equipment to be save on site for later reuse. Debris to be transported to the city dump site. Prior to transportation clearance for the items to be taken from the EULEX Representative. | LS | 1 |  | 0
4.13 | Demolition of the damaged floor layers for office containers and one 10'ablution unit (linoleum +plywood+steam blockade + insulation). Price should include transportation of debris to the city dump site. Note: Only if the floor panels are damaged. Each container is to be assessed jointly with EULEX Engineer during construction. | m2 | 147 |  | 0
4.14 | Provide, spread and compact gravel 0-30 for the ground floor corridor | m3 | 7.36 |  | 0
4.15 | Supply and install floor thermo insulation styrodur, 25 kg/m3 in thickness of 160 mm (2x80mm), throughout the ground floor corridor over the gravel. See dwg #20 | m2 | 37 |  | 0
4.16 | Supply and install PVC foil in one layer 0.2mm. Installation carried out as per manufacturer's instructions, overlapping at minimum 100mm in joints. Dwg A-04/A-05 | m2 | 37 |  | 0
4.17 | Provide material and construct reinforced concrete floor with flat uniformal finishing on the ground floor corridor and staircase area (Dwg A-04/A-05) Thickness 100mm, C20/25, reinforcement is calculated in price ( net Q335 150x150mm) | m2 | 37 |  | 0
4.18 | Provide material and construct concrete screed t=5cm thru the ground floor corridor and staircase area | m2 | 37 |  | 0
4.19 | Provide material and place 100mm mineral wool insulation throughout the office containers floors, ablution unit and above the containers between the trusses. | m2 | 190 |  | 0
4.2 | Provide material and install plastic sheet 0.2mm all over the office and ablution flooring. | m2 | 190 |  | 0
4.21 | Provide material and install 20mm thick plywood flooring throughout the office containers and first floor corridor surface. | m2 | 224 |  | 0
4.22 | Provide and install 20mm thick water-resistant plywood flooring for the ablution unit. | m2 | 6 |  | 0
4.23 | Provide material and install final coat flexible PVC,through the floor of the office containers t=2mm, including flooring of the refurbished ablution unit where the pvc is to be 15 cm height up to the wall. PVC is to be welded & glued with proper adhesive. Skirtings all around the perimeter of the surface is to be included in the price. Color to be chosen by EULEX Representative. PVC 2.0mm thick, commercial use, EN 649, classification as per EN 685 Class 33, areas with heavy traffic. | m2 | 147 |  | 0
4.24 | Provide material and construct corridor facade walls with the following materials: interior with plasterboards 2x12.5mm over metal studs, thermal insulation 100mm, metal structure 40mmx60mm as supporting structure, OSB plate 15mm, membrane for rain and wind protection, covered with metal sheet prepainted thickness 0.55mm as a facade from outside. Price shall include treatment of plaster boards and preparation of the surface for painting. Openings for foreseen doors and windows is to be prepared as per designs provided. Dwg. #19 & #21 | m2 | 24 |  | 0
4.25 | Provide material and construct first floor corridor structure consisting of iron rectangular profiles 60x40x3mm and 40x 40x2.6mm lengthwise, including L profiles 50x4mm lengthwise on both sides of the corridor, as per designs provided, dwg 22. The whole structure elements/profiles are to be made rust free, painted with antirust paint 2x.
| POZ 1 | EA | 1 |  | 0
| POZ 2 | EA | 1 |  | 0
| POZ 3 | EA | 1 |  | 0
| POZ 4 | EA | 1 |  | 0
4.26 | Provide material and construct support structure of first floor corridor ceiling consisting of wooden timber 100x80mm every ~60cm, installed between two peace's of steel L profiles 40x40 x 2mm welded in container/trusses structure, as per designs provided dwg #20. steel L profiles are to be made rust free, painted with antirust paint 2x, wooden timbers to be painted2x with wood protection paint. | m2 | 42.47 |  | 0
4.27 | Provide with material and install the UPE Steel profiles as a support for stairs and first floor structure as per dwg #21. The whole profiles are to be made rust free, painted with antirust paint 2x and final oil paint ,color RAL 9002 | kg | 217.5 |  | 0
4.28 | Provide material and construct complete interior staircase as per design provided. Price is to include treatment with antirust paint 2x and oil pain white 2x. (dwg 21). | LS | 1 |  | 0
4.29 | Provide material and install laminate flooring for the corridors of Ground and First floor, suitable for commercial use, resistant to scratches and water, with 5mm sponge under layer , th =8mm. Price to include appropriate skirting profiles throughout the building and also aluminum skirting at offices entrance/building entrance. Sample to be provided for approval prior to installation. | m2 | 78 |  | 0
4.3 | Provide material and seal the joints between containers for the double container rooms (walls/ceiling). Sealing is to be done with pre-painted flat metal sheet thickness 0.60mm. Prior to installation the gaps between two containers are to be filled with foam/mineral wool as required. Color similar to interior paint. | m' | 42.4 |  | 0
4.31 | Provide and install galvanized metal sheet strip 41cm wide t=2mm for covering the floor joints of double office containers. Prior to installation the gaps between two containers are to be filled with mineral wool as required | m' | 18 |  | 0
4.32 | Provide and install mineral fiber suspended ceiling panels dim 600x600 mm, first class quality, complete with all the necessary fixtures/supporters for the ground floor and first floor corridor. Sample to be provided for approval prior to installation. | m2 | 78 |  | 0
4.33 | Provide material and paint interior of all office/ablution units, including corridors initially with primer and then with acrylic enamel paint 2x. Paint characteristics: semi-gloss coating, eco-friendly, thinning with water. Paint is to be applied by spraying. Previously the surface is to be cleaned of dust and any debris. | m2 | 420 |  | 0
4.34 | Dismantling of existing AC window unit in all containers which is to be delivered to EULEX representative. After disassembly, the remaining gap with dim. 80 x 65cm is to be closed from inside and outside with 0.6 mm prepainted metal sheet with sufficient overlap and in the middle filled with styrodur t-60mm. | EA | 6 |  | 0
4.35 | Supply and install 12000 BTU split unit Air Conditioner, as per Technical Specifications. In the price to be calculated drilling of necessary holes, piping, wiring and brackets for AC. Note: due to the facade to be installed over the container panels the brackets to be provided for the outside unit and to be longer. | EA | 4 |  | 0
4.36 | Supply and install 9000 BTU split unit Air Conditioner, as per Technical Specifications. In the price to be calculated drilling of necessary holes, piping, wiring and brackets for AC. Note: due to the facade to be installed over the container panels the brackets to be provided for the outside unit are to be longer. | EA | 2 |  | 0
4.37 | Provide and replace all door cylinders (offices and ablution units). New cylinders should have minimum three keys, adjusting also the existing door lock. | EA | 9 |  | 0
4.38 | Provide and install external PVC double wing door. The main entrance door should be of PVC profiles as per design provided (dwg #15) DIM 230/240cm Glass: double, fully insulated, thermal protection, 6+12+4mm. Door is to be equipped with door lock complete, minimum three keys. | EA | 1 |  | 0
4.39 | Installation of Aluminum Emergency Exit doors dismantled from the Block #7, complete with push bar and hydraulic door closer. | Ea | 2 |  | 0
4.4 | Provide and install office PVC Window dim 95x125cm, as per design provided. Glass: double, fully insulated, thermal protection, 6+12+4mm (dwg 15), prior the container panel to be cut /old window to be dismantled. | EA | 15 |  | 0
4.41 | Provide and install toilet PVC Window dim 60x80cm, as per design provided. Glass: double, fully insulated, thermal protection, 6+12+4mm (dwg 15) prior the container panel to be cut. | EA | 4 |  | 0
4.42 | Provision and installation of room numbers (01 to 06) | EA | 6 |  | 0
4.43 | Provide with material, manufacture and install inside stairs all according to the drawing provided (See dwg.21) including the hand rails. | LS | 1 |  | 0
4.44 | Installation of Emergency exit staircase dismantled from the block #7, complete structure with rails, prior the cube concrete foundations 60x60x60cm with steel plate 300x300x10mm anchored on it (total 6 foundations). In the metal plate of foundation, columns of staircase are to be welded. In the price to be included any adjustment of elements during installation and painting with primary and final paint of the welded parts (Stairs are recently renovated and painted) | LS | 1 |  | 0
4.45 | Provide material and construct roof metal structure, consisting of trusses with profiles 60X40X3mm and 40x2.5mm including purlins 60X40X3mm as per design provided, dwg 20. In total 6 trusses are required . | Kg | 1500 |  | 0
4.46 | Provide and install pre-painted corrugated metal sheet of t=0.55mm as roof cover with drip stop layer. Price to include snow guards and roofing ridge cap which is to cover min. 30cm in both sides. Color RAL 9002. Slope surface calculated. | m2 | 154 |  | 0
4.47 | Provide and install pre-painted (piano) metal sheet roof eaves 50 cm overhang, of 0.50mm thickness. Color RAL 9002 (fascia and soffit all sides). | m2 | 30 |  | 0
4.48 | Provide and install half round horizontal rain gutters 150mm, from pre-painted metal sheet 0.6mm thickness. Color RAL9002. Price shall include as well provision and installation of hangers and all the required accessories. | m' | 22 |  | 0
4.49 | Provide and install vertical gutters ( Rainwater down pipes 100mm diameter), of pre-painted metal sheet 0.6mm thickness. Color RAL 9002. | m' | 24 |  | 0
4.5 | Provide and install pre-painted metal sheet roof edges/A sides 0.50mm thickness (piano). Color RAL 9002. Price shall include the required flushings where the two different height roofs meet and the roof ventilation grill. | m2 | 26 |  | 0
4.51 | provide with material and concreting of stairs at the entrance of the building with C-25/30 concrete, including frame works Dim 160x60(30+30) x h 32(16+16) cm | Ea | 1 |  | 0
4.52 | Provide and install kitchen sink -stainless still with cabinet, complete with proper tap for cold and hot water. Cabinet is to be from plywood, white color. Bench top to be plasticized and waterproof. In the price to be calculated all accessories for sink connection to the existing cold/hot water and sewerage system . Dim 120x60x90 | EA | 1 |  | 0
4.53 | Provide and install kitchen cabinet (working table) from white plywood, with upper working bench top from waterproof plasticized material. Dim 120x60x90 | EA | 1 |  | 0
Ablution Units 10'
4.54 | Provide and install single washing base in one of ablution units were is missing, complete functional (with faucet for cold and hot water, with rear overflow holes and other accessories). Modifications on the height (bolts) of the shower base is required in order to fit the sewerage pipes underneath. | EA | 1 |  | 0
4.55 | Provide with material and install sewerage pipe ᴓ50mm and water pvc pipe with tap adequate for dishwasher machine in two(2) F and M ablution units. Installation to be done in existing sewerage/water system | LS | 2 |  | 0
Facade works
4.56 | Remove existing metal holders connecting two containers, welding of the containers in between. Removed metal holders to be handed over to EULEX | LS | 1 |  | 0
4.57 | Provide materials and install lightweight façade made of expanded polystyrene plates 100mm thick ( over panels 80%) and 50mm(over columns 20%), with all necessary elements and layers including render finish and final paint, as per dwg #24 and technical specification according to DIN EN 13501 | m2 | 260 |  | 0
4.58 | Provide and install window sills of prepainted metal sheet 1mm. | m' | 17.5 |  | 0
4.59 | Provision and installation of scaffolding during the works including screen to secure particles/dust from spreading outside the working area. | LS | 1 |  | 0
Electrical Works
4.6 | Dismantling of the existing electrical/IT installations within the provided EULEX office containers. All the materials dismantled ( switches, lights, plugs) are to be handed over to EULEX Representative. Individual containers electrical panels are to not be dismantled, but to remain and be reused. Clearance for any removal of debris from the site is to be taken from the Project Manager of EULEX. | EA | 10 |  | 0
4.61 | Install main electrical panel for the building, complete with main switch AS 80A, circuit breaker 4x 32A tree poles and four(4) circuit breaker 16A. Price to include grounding of the panel with the material required. | EA | 1 |  | 0
4.62 | Provide material and install containers electrical connections (maximum 4 containers on a line), for the whole containerized building. Connections are to be done with cabling flexible 5x6mm2, directly in the fuse box inside the container. Prior the industrial plugs of 32 A are to be removed. | EA | 13 |  | 0
4.63 | Provide and install 5x6mm² cable with the required accessories to connect distribution boxes of double containers in between. Price to include cover of the cable ( trunking) | m' | 10 |  | 0
4.64 | Connection of containers in between with cable 1x35mm2 for earthling. | LS | 1 |  | 0
4.65 | Provide and install LED Flood light reflector 100W with all necessary cabling 3x1.5mm and dark censor of 10A. Installation to be done in entry part of roof A form, in galvanized metal poles fixed on the structure of the containers. Price to include circuit breakers, cabling, dark sensor, and other fittings as required. | EA | 1 |  | 0
4.66 | Provide and install single phase double socket outlets, wall/panel mounted, 16A, 220V. Price shall include cable type PPY 3x2,5mm² and all the required fittings for functional sockets. Cables are to be covered with proper PVC trunkings. | EA | 26 |  | 0
4.67 | Provide and install single phase single sockets, complete with required fittings 16A, 220V. Price shall include cable type PPY 3x2,5mm² and all the required fittings for functional sockets. Cables to be covered with PVC trunking. | EA | 12 |  | 0
4.68 | Provide and install single phase single sockets for AC's, complete with required fittings 16A, 220V. Price is to include all the cabling provision and installation PPY 3x2,5mm², with the required fittings. Cables to be covered with PVC trunking. | EA | 6 |  | 0
4.69 | Provide and install single phase single sockets suitable for toilets/IP65/with cover, complete with required fittings 16A, 220V. Price is to include all the cabling provision and installation PPY 3x2,5mm², with the required fittings. Cables to be covered with PVC trunking. | EA | 6 |  | 0
4.7 | Provide and install LED light fittings designed for suspended ceiling (60x60cm) , through the corridor of the building. Price is to include provision and installation of required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be placed over the suspended ceiling. | EA | 15 |  | 0
4.71 | Provide and install surface mounted LED lights, 1x40W (dim 30x120cm). Price is to include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC trunking. | EA | 60 |  | 0
4.72 | Provide and install surface mounted slim LED lights 40w within ablution units, IP65 Price shall include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC trunking. | EA | 2 |  | 0
4.73 | Provide and install surface mounted slim LED lights 40w IP 55 for the entrance. Price shall include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC trunking. | EA | 1 |  | 0
4.74 | Provide and install Emergency EXIT LED light 10W as per dwg provided, including cabling and all the trunking required. | EA | 3 |  | 0
4.75 | Provide and install Emergency LED light 10W as per dwg provided, including cabling and all the trunking required. | EA | 4 |  | 0
4.76 | Provide and install light switches 6A (single/double pole, and alternative ) mounted on wall panels with all required cabling/accessories for functional switch. | EA | 6 |  | 0
4.77 | Provide and install moving sensors for corridors and ablution units lights 360º, ceiling mounted with all required cabling/accessories for functional sensor. | EA | 9 |  | 0
4.78 | Provide and install electrical panel with 3 poles circuit breaker 32A, with supply cable 5x6mm2 from the main electrical panel, required for the IT Rack Cabinet. | EA | 1 |  | 0
Heating System
4.79 | Opening by hand the channel 50 x60cm from the corner of the infirmary block to the corner of new Commander block were the existing heating pipes DN 25 are to be removed. Excavated material to be saved on side for reuse. | M' | 8 |  | 0
4.8 | Provide and installation of pre-insulated heating pipes DN 32 in the opened channel from previse item with all necessary fittings for connection to the existing heating system. | m' | 16 |  | 0
4.81 | Design and build the heating system inside the building from Cu pipes with all necessary fittings, which are to be finally painted with white color heat resistant. Heating troups-rediators along with thermoheads, are to be used the dismantled ones from the Block#7( 15 radiator needed) | M' | 1 |  | 0
4.82 | Provide with material and assembly of pre-painted metal sheet boxes for protection of pipes at the entrance to the building reinforced with steel profiles 20x20x2mm, with door for access possibility. Dim. 40x60x30cm (see existing as example) | EA | 1 |  | 0
|  |  |  | Total | 0

## 5. Fence and Infrastructure
Reorganization of Mitrovica ECM
5 | T walls - fence and infrastructure works
| Works Description | Unit | Quantity | Unit price | Total price
5.1 | Relocation of T walls within the same Compound- from their current position to the new identified position as per existing and new designs provided creating the new division for the partial handover of the Camp. T wall footing 1.6m wide, T wall high 3.00m, length 1.5m'. Gravel bases needed to be provided and placed by contractor and is to be included in the price. | EA | 69 |  | 0
5.2 | Transportation of T walls from ECM to Prishtina EPC/ Dumosh TEC. T wall footing 1.6m wide, T wall high 3.00m, length 1.5m'. T walls are to be unloaded in the site designated by the project engineer. | EA | 73 |  | 0
5.3 | Provide with material and construction of new wall h 250 + V steel profiles and concertina wire ofᴓ 60cm( same as existing perimeter wall of entire camp), see dwg # 27, price to include excavation works in asphalted/concreted area and backfilling works around foundations. | m' | 118 |  | 0
5.4 | Provide with material and construction of new fence icluding V steel profiles and concertina wire ᴓ 60cm, all according to dwg # 27, Fence is to be installed on top of the remain wall in right side of vehicle entry( see item 2.3). | M' | 25.5 |  | 0
5.5 | Dismantle the 2.2m high fence around the heating plant near by block 7 and save on site for further use (10m' are to be reused-see pos. below, other 10m' are to be taken off from the compound.) | m' | 20 |  | 0
5.6 | Installation of dismantled fence from the previous pos, in new location, around the waste containers, adjusting the fence as needed with welding, paintig,and construction od new cube concrete foundations 40x40x30 +10cm compacted gravel, every ~3m' with anchored steel plate 200x200x5mm on top of cube foundation.. | m' | 10 |  | 0
5.7 | Provide with material and install the underground PE Septic tank for SSD block & for BI guards Ablution with capacity of 1000L. Septic Tank to be installed in the same place where the old one with smaller capacity is dismantled. In the price to be calculated excavation works( ~ 6m3 of earth), backfilling works after tank installation and top protection of the tank with reinforcement concrete slab with Q 226 mesh ( slab dim 250x250x10cm), with steel cover for the shaft . See tech. specs for more details. | EA | 1 |  | 0
Plumbing (Water &Sewerage) - exterior
5.8 | Conduct site survey and marking of the trench line on terrain as per the drawing provided for water and sewerage lines. | LS | 1 |  | 0
5.9 | Cutting of asphalt for the trench with adequate asphalt cutting machine, and removal of the cut asphalt from the site (asphalted trench length 92m) | m' | 106 |  | 0
5.1 | Removing the concrete pavement block , storing on site and reinstall again after finishing with canal works with installations. | M2 | 5 |  | 0
5.11 | Excavation of trenches to depth up to average 80 cm, over the entire route length with adequate excavator machine. Note and include in the price that under 20cm of land level exist underground reforcement concrete slab 20-30cm thickness that is to be broken, to create required depth of the tranch. Tranch as per marked line in dwg.#2. Excavated material is to be temporary storingon site, to be reused for backfilling. (total trench length 60m') Leftover material should be disposed of by the contractor from the site | m3 | 40 |  | 0
5.12 | Provide materials and lay 10cm thick sand bed (0.5-2mm grain size) to bottom of trenches, including leveling of upper surface and filling over pipes to a total of 30cm. | m3 | 15 |  | 0
5.13 | Provide and install PVC sewerage pipe 120mm for SSD and Toilet for BI guards- from objects to the septic tank and for FPU Commander Block- from object to the existing sewerage system. Calculation to be done for all exterior works including entry to the premises. | m' | 60 |  | 0
5.14 | Cut the concrete slab, open the hole ~100x100cm in depth of ~120cm, to reach the existing water supply pipe of 2". In same place is to be build the manhole (foreseen in Item 5.15) | LS | 1 |  | 0
5.15 | Provide and connect new PE 1" water pipe into the existing main pipe of 2", including all the accessories/fittings for conection. Calculation to be done for all exterior works including entry to the premises. | m' | 60 |  | 0
5.16 | Provide and install pre-fabricate concrete elements for manhole with diameter 1000/1000 & 600/1000 fixed on concrete base, including filling of joints, complete waterproof. Heavy duty manhole metal cover included (standard heavy transport 25t). Price to include excavation and refilling works | EA | 7 |  | 0
5.17 | Backfill the trenches with excavated material in 20 cm thick compacted layers. Surplus material is to be disposed outside EULEX compound. | m3 | 25 |  | 0
5.18 | Provision and installation of the sewerage underground warning tape throughout the trench, 30 cm below the finished surface. | m' | 60 |  | 0
5.19 | Provision and installation of the water underground warning tape, 30 cm below the finished surface. | m' | 60 |  | 0
5.2 | Providing and spreading gravel, particle size 0-30 mm on previously compacted sub-base and compacting to form a final base course of 250mm thickness. Compacting to be done with power roller note: total amount of the gravel is to be calculated in final compacted state | m3 | 25 |  | 0
5.21 | Placing back the peevishly removed concrete pavement blocks ( point 1.3) | m2 | 20 |  | 0
5.22 | Provide and spread layer of bitumen emulsion (hot coat) above base course of compacted gravel, average 0,8kg/m2 for better connection between road base course and layer of asphalt. | m2 | 48 |  | 0
5.23 | Provide material and laying of asphalt layer 80mm finished thickness after consolidation by power roller , mixture 0-16mm including compaction. | m2 | 48 |  | 0
5.24 | Provision and installation of heat trace for all over ground pipes/ entry points to the premises. | m' | 12 |  | 0
5.25 | Insulation of all over ground pipes/entry points to the buildings | LS | 1 |  | 0
Electrical
5.26 | Cutting of asphalt for the trench with adequate asphalt cutting machine, and removal of the cut asphalt from the site. | m' | 90 |  | 0
5.27 | Removing the concrete pavement block , storing on site and reinstall again after finishing with canal works with installations. | M2 | 9.5 |  | 0
5.28 | Excavation of trenches 60 cm wide and 60 cm deep for the underground cabling. Note and include in the price that under 20cm of land level exist underground reforcement concrete slab 20-30cm thickness that is to be broken, to create required depth of the trench. Trench as per marked line in dwg.#2 , total 73m' (due to the many underground cables, hand excavation nearby the server room is to be foreseen) | m3 | 26.3 |  | 0
5.29 | Provide material and laying of sand base (under, around and over the ducting pipes, 20cm ) throughout the all trenches. | m3 | 8.8 |  | 0
5.3 | Provide and install ducting corrugated pipe Ø75mm equipped with rope/wire, throughout the trenches, from main electrical panel installed in Reception(see pos. 5.30) to the electrical panels of : Reception block, SSD block, Server room#8, containers for reserve food and water and up to the second entry gate (see dwg.#2) In every trench are to be installed 3 ducting pipes, one of them will be used for IT and Comms cabling. | m' | 330 |  | 0
5.31 | Provide material and construct concrete manhole complete 1000 depth dim1000x1000m , including heavy duty metal covers 600x600mm (25T) and other required works to make the manholes functional - for purpose of laying down all the installations to the buildings. | EA | 2 |  | 0
5.32 | Provide with material and install Electrical Panel #1withIP65, equipped with cartridge 250A and knife fuses 3pcs. Grounding of the panel, to be done with copper rod | EA | 1
5.33 | Disconnect the existing electrical cable NYY-J (PP00) 4x120mm2 Copper from block#7, pull the cabling from the shaft nearby reception block and redirect the cable to word the Reception block as shown in dwg#2. Cable is to be connected to the electrical panel #1 from pos.5.31. Price to include all necessary fittings for connection. | LS | 1 |  | 0
5.34 | Provide material and install underground cable 4x16mm2 (Cu) from electrical panel #1 up to el.panels of SSDblock, Reception block, Server Room#8, two security containers and up to the second entry gate. Price to include connection of the cables in both ends with all necessary fittings. | m' | 80 |  | 0
5.35 | Backfill the trenches with excavated material in 20 cm thick compacted layers. Surplus material is to be disposed outside EULEX compound. | m3 | 8.8 |  | 0
5.36 | Supply and laying of the underground warning tape throughout the all trenches. | m' | 80 |  | 0
5.37 | Providing and spreading gravel, particle size 0-30 mm on previously compacted sub-base and compacting to form a final base course of 20cm thickness. Compacting to be done with power roller note: total amount of the gravel is to be calculated in final compacted state | m3 | 8.8 |  | 0
5.38 | Provide and spread layer of bitumen emulsion (hot coat) above base course of compacted gravel, average 0,8kg/m2 for better connection between road base course and layer of asphalt. | m2 | 44 |  | 0
5.39 | Provide material and laying of asphalt layer 80mm finished thickness after consolidation by power roller , mixture 0-16mm including compaction. | m2 | 44 |  | 0
5.4
5.41
5.42 | Dismantling of existing steel poles100x100mm, 6m high togethet with reflectors and censors, from Twalls and installation of the same to the new Twall/wall fence line together with lights/reflectors censor, as per instruction of site Engineer. Price to include painting of the poles with primary and final oil paint . | EA | 5 |  | 0
5.43 | Provide and install new elect. Cable for the fence reflectors 5x2.5mm. Cabling is to be o be covered with proper PVC trunking. | m' | 200 |  | 0
5.44 | Provide and install new elect. Cable for the fence reflectors 3x1.5mm. Cabling is to be covered with proper PVC trunking. | m' | 100 |  | 0
5.45 | Dismantling of existing steel poles 100x100mm, 6m high together with cameras from Twalls and reinstallation of the same to the new Twall/wall /fence line together with cameras, as per instruction of site Engineer. Price to include painting of the poles with primary and final oil paint . | EA | 4 |  | 0
|  |  |  | Total | 0

## 6. ITComm
Reorganization of Mitrovica ECM
6 | IT/Comms Works
| Works Description | Unit | Quantity | Unit price | Total price
6.1 | IT/COMMS Internal Network is to be designed and build for the new Blocks: SSD Block, Reception Block and FPU Commanders Block as per technical specifications provided. Indoor works include providing internal building wiring, star structure using STP cables from office space outlets to a centralized, single per building Intermediate Distribution Frame (IDF). Requirements of outlets: Minimum 3 dual outlets for single container Minimum 5 dual outlets for double container Minimum 2 dual outlets for ground floor corridor Minimum 2 dual outlets for 1st floor corridor. Contractor to desing, build and test all internal network complete. It will be responsibility of EULEX to bring the exterior cable up to the installed IDF for the building. | LS | 1 |  | 0
|  |  |  | Total | 0

## 7-FPU Ablution Units
Reorganization of Mitrovica ECM
7 | FPU Ablution Units in residential blocks
| Works Description | Unit | Quantity | Unit price | Total price
7.1 | 20' Ablution Units in R1 & R2 (4 Units) Ground Floor-Dwg. A02 &A09
7.1.1 | Dismantling/demolition of electrical installation from the ceiling and walls. Debris to be transported to the city dump site. Prior to transportation clearance for the items to be taken from the EULEX Representative. Price per Ablution Unit | LS | 4 |  | 0
7.1.2 | Demolition of the complete partition walls and sanitary equipment , showers, washing bases, toilets, mirrors, urinals, water heater complete with old water and sewerage network. Debris to be transported to the city dump site. Prior to transportation clearance for the items to be taken from the EULEX Representative. | LS | 4 |  | 0
7.1.3 | Demolition of the complete floor layers with structure from the ablution units (laminate/plywood+steam blockade+insulation+metal structure with metal sheets ). Price should include transportation of debris to the city dump site. | m2 | 56 |  | 0
7.1.4 | Provide material and place the 50cm thick compacted gravel 0-30mm below the removed flooring panels. At the price to be calculated closing of the gap under the containers so that the gravel does not spill beyond the containers | m3 | 30 |  | 0
7.1.5 | Provide and place flexible plastic sheet 0.2mm all over the gravel surface | m2 | 56 |  | 0
7.1.6 | provide material and construction of the concrete slab MB 30, thickness 10cm, reinforced with steel mesh Q283(ᴓ6mm/100 mm) | m2 | 56 |  | 0
7.1.7 | provide with material and laying of the concrete screed (estrich) thickness 4cm over the concrete slab | m2 | 56 |  | 0
7.1.8 | Provide with material and build the strip with siporex blocks to separate the showers as per drawing provided. Strip cross section 7.5x10cm. | m' | 38 |  | 0
7.1.9 | Provide and install hydro-insulation of flooring with two component liquid insulation in two coat. Also apply two coat of insulation 12 cm high in the perimeter walls and all sides of the strip with siporex blocks. | m2 | 76 |  | 0
7.1.10 | Provide material and paint walls and ceiling initially with primer and then with acrylic enamel paint 2x. Paint characteristics: semi-gloss coating, eco-friendly, thinning with water. Paint is to be applied by spraying. Previously the surface is to be cleaned of dust/rust and any holes to be repaired. after cleaning, rusted area to be treated with anti-rust paint. As well all equipment, windows, etc., are to be properly protected prior painting. Painted wall should be washable. | m2 | 220 |  | 0
7.1.11 | Provide and install non slippery ceramic tiles R10 for toilets over the concrete screed including skirting in high 12cm with same ceramic tiles as flooring. In the price to be calculated adequate glue for installation and ceramic joint material "Fugomall". Colouring of ceramic tiles will be assigned by Contracting Authority. | m2 | 56 |  | 0
7.1.12 | Provide with material and install skirting's in height of 12cm with same ceramic tiles as flooring along the entire perimeter of the wall | M' | 67.2 |  | 0
7.1.13 | Provide with material and cover with ceramic tile the strip of siporex blocks in all 3 sides, including proper angle skirtings. Tiles to be same as flooring tiles | m' | 38 |  | 0
7.1.14 | Provide and install shower partitions as per dwg provided. Partitions are to be of waterproof compacted panels with thickness -12mm, impact and scratch resistant, waterproof, easy to clean, bacteria resistant, color white, finish – mat. Partition of showers should end 10cm below the ceiling . Profiles to be used are to be square clear anodized aluminum profiles, resists to corrosion, mold and fungus. Urinal partitions are to be of the same material as well. | m2 | 55 |  | 0
7.1.15 | Supply and install the PVC curtains white color with stainless steel pipe holder for showers. | EA | 20 |  | 0
7.1.16 | Provide and install the shower set with valve, complete with shower heads and flexible hoses (wall hanged as well), water tap and other accessories for proper operation. | EA | 20 |  | 0
7.1.17 | Provide and install single washing base complete functional, with faucet for cold and hot water, with rear overflow holes and other accessories. | EA | 8 |  | 0
7.1.18 | Provide and install new urinals complete with faucets. Urinals shall be wall-hung washout urinal, flushing rim, integral trap and shall be provided complete with manual flusher . | EA | 8 |  | 0
7.1.19 | Provide and install mirrors over each washbasin , dim 60/40cm | EA | 8 |  | 0
7.1.20 | Provide and install new floor drain (2 in each ab.Unit) and showers drain(5 in each Abl. Unit) with stainless steel cover with 50mm OD outlet | EA | 28 |  | 0
7.1.21 | Provide and install boiler 300ltr with conection to the water network. In the price to be calculated three polar separate circuit breaker and necessary cabling for connection. Cabling is to be covered with proper PVC piping. | EA | 4 |  | 0
7.1.22 | Design and build water supply network with connections from the main water pipes which is close to the building to each ablution/sanitary element as per drawing provided. Price to include all the required fittings for functional ablution unit Price per 4(four) ablutions. | LS | 1 |  | 0
7.1.23 | Design and build sewerage system with connections from the existing sewerage network which is close the building to each ablution/sanitary element as per drawing provided. Price to include outside sewerage pipe as the existing one is above the flooring level, with all the required fitting and conections for functional ablution unit. Price per 4(four) ablutions. | LS | 1 |  | 0
7.1.24 | Closing the facade holes after removing the old sewerage pipes (the old network lies on the floor while the new one will lie under the floor, the penetration into the facade will not be in the same place). The holes are to be closed nicely, to reach same surface as other part of the building. | EA | 4 |  | 0
7.1.25 | Provide and install single phase sockets suitable for toilets/IP65/with cover, complete with required fittings 16A, 220V. Price is to include all the cabling provision and installation PPY 3x2,5mm², with the required fittings. Cables to be covered with PVC piping. | EA | 16 |  | 0
7.1.26 | Provide and install surface mounted LED lights for toilets, IP65, water resistant, 1x40W (dim 30x120cm). Price is to include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm². Cabling is to be covered with proper PVC piping. | EA | 8 |  | 0
7.1.27 | Provide and install moving sensors for ablution units lights 360º, surface mounted with all required accessories and necessary cabling for functional sensor . Cabling is to be covered with proper PVC piping. | EA | 4 |  | 0
7.1.28 | Provide and install new radiator dim 100/60cm in existing heating network, previously the old one to be dismantled. New radiator is to be equipped with thermo-head regulator. In the price to be calculated painting of existing heating pipes inside ablution unit with white color, heat resistant. | EA | 4 |  | 0
7.2 | 10' Ablution Units in R1&R2 (6 Units) Ground Floor -Dwg. A03 & A09
7.2.1 | Dismantling/demolition of electrical installation from the ceiling and walls. Debris to be transported to the city dump site. Prior to transportation clearance for the items to be taken from the EULEX Representative. Price per Ablution Unit | LS | 6 |  | 0
7.2.2 | Dismantling/demolition of the sanitary equipment , showers, washing bases, toilets, mirrors, water heater complete with old water and sewerage network. Debris to be transported to the city dump site. Prior to transportation clearance for the items to be taken from the EULEX Representative. | LS | 6 |  | 0
7.2.3 | Demolition of the complete floor layers with structure from the ablution units (laminate/plywood+steam blockade+insulation+metal structure with metal sheets ). Price should include transportation of debris to the city dump site. | m2 | 36 |  | 0
7.2.4 | Provide material and place the 50cm thick compacted gravel 0-30mm below the removed flooring panels. At the price to be calculated closing of the gap under the containers so that the gravel does not spill beyond the containers | m3 | 17 |  | 0
7.2.5 | Provide and place flexible plastic sheet 0.2mm all over the gravel surface | m2 | 36 |  | 0
7.2.6 | provide material and construction of the concrete slab MB 30, thickness 10cm, reinforced with steel mesh Q283(ᴓ6mm/100 mm) | m2 | 36 |  | 0
7.2.7 | provide with material and laying of the concrete screed (estrich) thickness 4cm over the concrete slab | m2 | 36 |  | 0
7.2.8 | Provide and install hydro-insulation of flooring with two component liquid insulation in two coat. Also apply two coat of insulation 12 cm high in the perimeter walls. | m2 | 43 |  | 0
7.2.9 | Provide material and paint walls and ceiling initially with primer and then with acrylic enamel paint 2x. Paint characteristics: semi-gloss coating, eco-friendly, thinning with water. Paint is to be applied by spraying. Previously the surface is to be cleaned of dust/rust and any holes to be repaired. after cleaning, rusted area to be treated with anti-rust paint. As well all equipment, windows, etc., are to be properly protected prior painting. Painted wall should be washable. | m2 | 180 |  | 0
7.2.10 | Provide and install non slippery ceramic tiles R10 for toilets over the concrete screed. In the price to be calculated adequate glue for installation and ceramic joint material "Fugomall". Colouring of ceramic tiles will be assigned by Contracting Authority. | m2 | 36 |  | 0
7.2.11 | Provide with material and install skirting's in height of 12cm with same ceramic tiles as flooring along the entire perimeter of the wall | M' | 60 |  | 0
7.2.12 | Provide and install toilet partitions as per dwg provided. Toilet partitions/door are to be of waterproof compacted panels with thickness -12mm. Compacted panel are to be impact and scratch resistant, waterproof, easy to clean, bacteria resistant, color white, finish – mat, doors dim. 70cm*195 furnished with a toilet lock (free/occupied). Pedestal type stainless steel legs. Profiles to be used are to be square clear anodized aluminum profiles, resists to corrosion, mold and fungus. | m2 | 50 |  | 0
7.2.13 | Provide and install single washing base complete functional (with faucet for cold and hot water, with rear overflow holes and other accessories) | EA | 6 |  | 0
7.2.14 | Provide and install mirrors over each washbasin , dim 60/40cm | EA | 6 |  | 0
7.2.15 | Provide and install boiler 10ltr for each washing base | EA | 6 |  | 0
7.2.16 | Provide and install new floor drain with stainless steel cover dim. 200x200mm with 50mm OD outlet | EA | 6 |  | 0
7.2.17 | Provide and install new toilets complete with flushing tank and built-in bidet tube. All water closets for toilets as shown on the drawings shall be dual function flush tank with built-in bidet tube, white, with complete fittings and mounting accessories | EA | 12 |  | 0
7.2.18 | Design and build water supply network with connections from the main water pipes which is close to the building to each ablution/sanitary element as per drawing provided. Price to include all the required fittings for functional ablution unit Price per 6(six) ablution. | LS | 1 |  | 0
7.2.19 | Design and build sewerage system with connections from the existing sewerage network which is close the building to each ablution/sanitary element as per drawing provided. Price to include all the required fitting for functional ablution unit. For more details, refer to the technical specification. Price per6(six) ablution. | LS | 1 |  | 0
7.2.20 | Closing the facade holes after removing the old sewerage pipes (the old network lies on the floor while the new one will lie under the floor, the penetration into the facade will not be in the same place). The holes are to be closed nicely, to reach same surface as other part of the building. | EA | 6 |  | 0
7.2.21 | Provide and install single phase single sockets suitable for toilets/IP65/with cover, complete with required fittings 16A, 220V. Price is to include all the cabling provision and installation PPY 3x2,5mm², with the required fittings. Cables to be covered with PVC piping. | EA | 12 |  | 0
7.2.22 | Provide and install surface mounted LED lights for toilets, IP65, water resistant, 1x40W (dim 30x120cm). Price is to include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC piping. | EA | 6 |  | 0
7.2.23 | Provide and install surface mounted LED lights for toilets, IP65, water resistant, 1x18W (dim 10x60cm). Price is to include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC piping. | EA | 12 |  | 0
7.2.24 | Provide and install moving sensors for ablution units lights 360º, surface mounted with all required accessories and necessary cabling for functional sensor . Cabling is to be covered with proper PVC piping. | EA | 18 |  | 0
7.2.25 | Provide and install new radiator dim 60/60cm in existing heating network, previously the old one to be dismantled. New radiator is to be equipped with thermo-head regulator. In the price to be calculated painting of existing heating pipes inside ablution unit with white color, heat resistant. | EA | 6 |  | 0
7.3 | 10' Ablution Units in R3&O1 (7 Units) Ground Floor -Dwg. A04 & A10
7.3.1 | Dismantling/demolition of electrical installation from the ceiling and walls. Debris to be transported to the city dump site. Prior to transportation clearance for the items to be taken from the EULEX Representative. Price per Ablution Unit | LS | 7 |  | 0
7.3.2 | Dismantling/demolition of the sanitary equipment , showers, washing bases, toilets, mirrors, water heaters complete with old water and sewerage network. Debris to be transported to the city dump site. Prior to transportation clearance for the items to be taken from the EULEX Representative. | LS | 7 |  | 0
7.3.3 | Demolition of the complete floor layers with structure from the ablution units (laminate/plywood+steam blockade+insulation+metal structure with metal sheets ). Price should include transportation of debris to the city dump site. | m2 | 42 |  | 0
7.3.4 | Provide material and place the 50cm thick compacted gravel 0-30mm below the removed flooring panels. At the price to be calculated closing of the gap under the containers so that the gravel does not spill beyond the containers | m3 | 22 |  | 0
7.3.5 | Provide and place flexible plastic sheet 0.2mm all over the gravel surface | m2 | 41 |  | 0
7.3.6 | provide material and construction of the concrete slab MB 30, thickness 10cm, reinforced with steel mesh Q283(ᴓ6mm/100 mm) | m2 | 41 |  | 0
7.3.7 | provide with material and laying of the concrete screed (estrich) thickness 4cm over the concrete slab | m2 | 41 |  | 0
7.3.8 | Provide with material and build the strip with siporex blocks to separate the showers as per drawing provided. Strip cross section 7.5x10cm. | m' | 14 |  | 0
7.3.9 | Provide and install hydro-insulation of flooring with two component liquid insulation in two coat. Also apply two coat of insulation 12 cm high in the perimeter walls.and all sides of the strip with siporex blocks. | m2 | 52 |  | 0
7.3.10 | Provide material and paint walls and ceiling initially with primer and then with acrylic enamel paint 2x. Paint characteristics: semi-gloss coating, eco-friendly, thinning with water. Paint is to be applied by spraying. Previously the surface is to be cleaned of dust/rust and any holes to be repaired. after cleaning, rusted area to be treated with anti-rust paint. As well all equipment, windows, etc., are to be properly protected prior painting. Painted wall should be washable. | m2 | 220 |  | 0
7.3.11 | Provide and install non slippery ceramic tiles R10 for toilets over the concrete screed including skirting in high 12cm with same ceramic tiles as flooring. In the price to be calculated adequate glue for installation and ceramic joint material "Fugomall". Colouring of ceramic tiles will be assigned by Contracting Authority. | m2 | 41 |  | 0
7.3.12 | Provide with material and install skirting's in height of 12cm with same ceramic tiles as flooring along the entire perimeter of the wall | M' | 70 |  | 0
7.3.13 | Provide with material and cover with ceramic tile the strip of siporex blocks in all 3 sides, including proper angle skirtings. Tiles to be same as flooring tiles | m' | 14 |  | 0
7.3.14 | Provide and install shower partitions as per dwg provided. Partitions are to be of waterproof compacted panels with thickness -12mm, impact and scratch resistant, waterproof, easy to clean, bacteria resistant, color white, finish – mat. Partition of showers should end 10cm below the ceiling . Profiles to be used are to be square clear anodized aluminum profiles, resists to corrosion, mold and fungus. | m2 | 16 |  | 0
7.3.15 | Supply and install the PVC curtains white color with stainless steel pipe holder for showers. | EA | 7 |  | 0
7.3.16 | Provide and install the shower set with valve, complete with shower heads and flexible hoses (wall hanged as well), water tap and other accessories for proper operation. | EA | 7 |  | 0
7.3.17 | Provide and install single washing base complete functional, with faucet for cold and hot water, with rear overflow holes and other accessories. | EA | 7 |  | 0
7.3.18 | Provide and install mirrors over each washbasin , dim 60/40cm | EA | 7 |  | 0
7.3.19 | Provide and install new toilets complete with flushing tank and built-in bidet tube. All water closets for toilets as shown on the drawings shall be dual function flush tank with built-in bidet tube, white, with complete fittings and mounting accessories | EA | 7 |  | 0
7.3.20 | Provide and install new floor and showers drain with stainless steel cover | EA | 14 |  | 0
7.3.21 | Provide and install boiler 200ltr for R3 with conection to the water network. In the price to be calculated three polar separate circuit breaker and necessary cabling for connection. Cabling is to be covered with proper PVC piping. | EA | 1 |  | 0
7.3.22 | Provide and install boiler 300ltr for O1 with conection to the water network. In the price to be calculated three polar separate circuit breaker and necessary cabling for connection. Cabling is to be covered with proper PVC piping. | EA | 1 |  | 0
7.3.23 | Design and build water supply network with connections from the main water pipes which is close to the building to each ablution/sanitary element as per drawing provided. Price to include all the required fittings for functional ablution unit Price per 7(seven) ablutions. | LS | 1 |  | 0
7.3.24 | Design and built sewerage system with connections . The connection to the existing sewerage network is immediately near the outer wall of the unit. Price to include all the required fitting for functional ablution unit. For more details, refer to the technical specification. Price per 7 (seven) ablutions. | LS | 1 |  | 0
7.3.25 | Closing the facade holes after removing the old sewerage pipes (the old network lies on the floor while the new one will lie under the floor, so the penetration into the facade will not be in the same place). The holes are to be closed nicely, to reach same surface as other part of the building. | EA | 7 |  | 0
7.3.26 | Provide and install single phase single sockets suitable for toilets/IP65/with cover, complete with required fittings 16A, 220V. Price is to include all the cabling provision and installation PPY 3x2,5mm², with the required fittings. Cables to be covered with PVC piping. | EA | 14 |  | 0
7.3.27 | Provide and install surface mounted LED lights for toilets, IP65, water resistant, 1x40W (dim 30x120cm). Price is to include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC piping. | EA | 7 |  | 0
7.3.28 | Provide and install moving sensors for ablution units lights 360º, surface mounted with all required accessories and necessary cabling for functional sensor . Cabling is to be covered with proper PVC piping. | EA | 7 |  | 0
7.3.29 | Provide and install new radiator dim 60/60cm in existing heating network, previously the old one to be dismantled. New radiator is to be equipped with thermo-head regulator. In the price to be calculated painting of existing heating pipes inside ablution unit with white color, heat resistant. | EA | 7 |  | 0
7.4 | 10' Ab. U. in R1;R2;R3;O1 (13 Units) Ist Floor -Dwg. A02; A03; A04; A05 &A10
7.4.1 | Dismantling/demolition of electrical installation from the ceiling and walls. Debris to be transported to the city dump site. Prior to transportation clearance for the items to be taken from the EULEX Representative. Price per Ablution Unit | LS | 13 |  | 0
7.4.2 | Dismantling/demolition of the sanitary equipment , showers, washing bases, toilets, mirrors, water heater complete with old water and sewerage network. Debris to be transported to the city dump site. Prior to transportation clearance for the items to be taken from the EULEX Representative. | LS | 13 |  | 0
7.4.3 | Demolition of the complete floor layers from the existing 10' ablution unit (pvc flooring/plywood +steam blockade+insulation). Price should include transportation of debris to the city dump site. | m2 | 78 |  | 0
7.4.4 | Provide material and place 100mm stone wool insulation throughout the ablution units | m2 | 78 |  | 0
7.4.5 | Provide material and install plastic sheet 0.2mm all over the office and ablution flooring. | m2 | 78 |  | 0
7.4.6 | Provide and install 20mm thick water-resistant plywood flooring for the ablution units. | m2 | 78 |  | 0
7.4.7 | Provision of material and installation of final coat flexible PVC through the floor of the ablution units. Compact and acoustic flexible covering 2.00mm thickness suitable for use in Healthcare facilities as per EN649/EN651 . PVC is to be welded & glued with proper adhesive with minimum 15 centimeters rise up to the walls . Skirtings all around the perimeter of the surface is to be included in the price. Color to be chosen by EULEX Representative. | m2 | 96 |  | 0
7.4.8 | Provide material and paint walls and ceiling initially with primer and then with acrylic enamel paint 2x. Paint characteristics: semi-gloss coating, eco-friendly, thinning with water. Paint is to be applied by spraying. Previously the surface is to be cleaned of dust/rust and any holes to be repaired. after cleaning, rusted area to be treated with anti-rust paint. As well all equipment, windows, etc., are to be properly protected prior painting. Painted wall should be washable. | m2 | 360 |  | 0
7.4.9 | Provide and install shower partitions as per dwg provided. Partitions are to be of waterproof compacted panels with thickness -12mm, impact and scratch resistant, waterproof, easy to clean, bacteria resistant, color white, finish – mat. Partition of showers should end 10cm below the ceiling . Profiles to be used are to be square clear anodized aluminum profiles, resists to corrosion, mold and fungus. | m2 | 28 |  | 0
7.4.10 | Provide and install boiler 200ltr for R1; R2; R3, with conection to the water network. In the price to be calculated three polar separate circuit breaker and necessary cabling for connection. Cabling is to be covered with proper PVC piping. | EA | 3 |  | 0
7.4.11 | Provide and install boiler 300ltr for O1, in the price to be calculated three polar separate circuit breaker and necessary cabling for connection. Cabling is to be covered with proper PVC piping. | EA | 1 |  | 0
7.4.12 | Provide and install new toilets complete with flushing tank and built-in bidet tube. All water closets for toilets as shown on the drawings shall be dual function flush tank with built-in bidet tube, white, with complete fittings and mounting accessories | EA | 13 |  | 0
7.4.13 | Provide and install single washing base complete functional, with faucet for cold and hot water, with rear overflow holes and other accessories. | EA | 13 |  | 0
7.4.14 | Provide and install mirrors over each washbasin , dim 60/40cm | EA | 13 |  | 0
7.4.15 | Provide and install the shower base dim 90x90 cm complete with shower heads and flexible hoses (wall hanged as well), water tap and other accessories for proper operation. Modifications on the height (bolts) of the shower basis are required in order to fit the sewerage pipes | EA | 13 |  | 0
7.4.16 | Supply and install the PVC curtains white color with stainless steel pipe holder for showers. | EA | 13 |  | 0
7.4.17 | Provide and install new floor drain with stainless steel cover with 50mm OD outlet | EA | 13 |  | 0
7.4.18 | Reinforcement of base for water drain with steel profiles welding in existing structure of the container. Profiles are to be anti-rust painted in two layers. For 1(one) container is needed 1.5m' of steel profile 40x20x2mm. | Ea | 13 |  | 0
7.4.19 | Design and build water supply network with connections to the existing network which is in outer wall of the unit. Price to include all the required fittings for functional ablution unit Price per 13 (thirteen) ablution. | LS | 1 |  | 0
7.4.20 | Design and built sewerage system with connections . The connection to the existing sewerage network is in outer wall of the unit. Price to include all the required fitting for functional ablution unit . Price per 13 (thirteen) ablution. | LS | 1 |  | 0
7.4.21 | Provide and install single phase sockets suitable for toilets/IP65/with cover, complete with required fittings 16A, 220V. Price is to include all the cabling provision and installation PPY 3x2,5mm², with the required fittings. Cables to be covered with PVC piping. | EA | 26 |  | 0
7.4.22 | Provide and install surface mounted LED lights for toilets, IP65, water resistant, 1x40W (dim 30x120cm). Price is to include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC piping | EA | 13 |  | 0
7.4.23 | Provide and install moving sensors for ablution units lights 360º, surface mounted with all required accessories and necessary cabling for functional sensor . Cabling is to be covered with proper PVC piping. | EA | 13 |  | 0
7.4.24 | Provide and install new radiator dim 60/60cm in existing heating network, previously the old one to be dismantled. New radiator is to be equipped with thermo-head regulator. In the price to be calculated painting of existing heating pipes inside ablution unit with white color, heat resistant. | EA | 13 |  | 0
7.5 | 20' Ablution Units in Rn Ground & I-st Floor -Dwg. A06 & A11
Ablution marked "A"
7.5.1 | Dismantling/demolition of electrical installation from the ceiling and walls. Debris to be transported to the city dump site. Prior to transportation clearance for the items to be taken from the EULEX Representative. Price per Ablution Unit | M2 | 1 |  | 0
7.5.2 | Demolition of the complete partition walls and sanitary equipments , showers, washing bases, toilets, mirrors, urinals, water heater complete with old water and sewerage network. Debris to be transported to the city dump site. Prior to transportation clearance for the items to be taken from the EULEX Representative. | LS | 1 |  | 0
7.5.3 | Demolition of the complete floor layers with structure from the ablution units (laminate/plywood+steam blockade+insulation+metal structure with metal sheets ). Price should include transportation of debris to the city dump site. | m2 | 14 |  | 0
7.5.4 | Provide material and place the 50cm thick commpacted gravel 0-30mm below the removed flooring panels. At the price to be calculated closing of the gap under the containers so that the gravel does not spill beyond the containers | m3 | 7.5 |  | 0
7.5.5 | Provide and place flexible plastic sheet 0.2mm all over the gravel surface | m2 | 14 |  | 0
7.5.6 | provade material and construction of the concrete slab MB 30, thickness 10cm, reinforced with steel mesh Q283(ᴓ6mm/100 mm) | m2 | 14 |  | 0
7.5.7 | provide with material and laying of the concrete screed (estrich) thickness 4cm over the concrete slab | m2 | 14 |  | 0
7.5.8 | Provide with material and build the strip with siporex blocks to separate the showers as per drawing provided. Strip cross section 7.5x10cm. | m' | 4 |  | 0
7.5.9 | Provide and install hydro-insulation of flooring with two component liquid insulation in two coat. Also apply two coat of insulation 12 cm high in the perimeter walls.and all sides of the strip with siporex blocks. | m2 | 17.5 |  | 0
7.5.10 | Provide material and paint walls and ceiling initially with primer and then with acrylic enamel paint 2x. Paint characteristics: semi-gloss coating, eco-friendly, thinning with water. Paint is to be applied by spraying. Previously the surface is to be cleaned of dust/rust and any holes to be repaired. after cleaning, rusted area to be treated with anti-rust paint. As well all equipment, windows, etc., are to be properly protected prior painting. Painted wall should be washable. | m2 | 55 |  | 0
7.5.11 | Provide and install non slippery ceramic tiles R10 for toilets over the concrete screed including skirting in high 12cm with same ceramic tiles as flooring.In the price to be calculated adequate glue for installation and ceramic joint material "Fugomall". Colouring of ceramic tiles will be assigned by Contracting Authority. | m2 | 14 |  | 0
7.5.12 | Provide with material and install skirting's in height of 12cm with same ceramic tiles as flooring along the entire perimeter of the wall | M' | 17 |  | 0
7.5.13 | Provide with material and cover with ceramic tile the strip of siporex blocks in all 3 sides, including proper angle skirtings. Tiles to be same as flooring tiles | m' | 4 |  | 0
7.5.14 | Provide and install shower/toilet partitions as per dwg provided. Partitions are to be of waterproof compacted panels with thickness -12mm, impact and scratch resistant, waterproof, easy to clean, bacteria resistant, color white, finish – mat. Partition of showers should end 10cm below the ceiling . Partition of toilets pedestal type stainless steel legs, doors dim. 70cm*195 furnished with a toilet lock (free/occupied) Profiles to be used are to be square clear anodized aluminum profiles, resists to corrosion, mold and fungus. Urinal partitions are to be of the same material as well. | m2 | 22 |  | 0
7.5.15 | Supply and install the PVC curtains white color with stainless steel pipe holder for showers. | EA | 2 |  | 0
7.5.16 | Provide and install new floor and showers drain with stainless steel cover with 50mm OD outlet | EA | 3 |  | 0
7.5.17 | Provide and install the shower set with valve, complete with shower heads and flexible hoses (wall hanged as well), water tap and other accessories for proper operation. | EA | 2 |  | 0
7.5.18 | Provide and install new urinals complete with faucets. Urinals shall be wall-hung washout urinal, flushing rim, integral trap and shall be provided complete with manual flusher . | EA | 1 |  | 0
7.5.19 | Provide and install single washing base complete functional (with faucet for cold and hot water, with rear overflow holes and other accessories) | EA | 2 |  | 0
7.5.20 | Provide and install mirrors over each washbasin , dim 60/40cm | EA | 2 |  | 0
7.5.21 | Provide and install new toilets complete with flushing tank and built-in bidet tube. All water closets for toilets as shown on the drawings shall be dual function flush tank with built-in bidet tube, white, with complete fittings and mounting accessories | EA | 3 |  | 0
7.5.22 | Provide and install boiler 200ltr with conection to the water network. In the price to be calculated three polar separate circuit breaker and necessary cabling for connection. Cabling is to be covered with proper PVC piping. | EA | 1 |  | 0
7.5.23 | Design and built water supply network with connections to the existing network. The connection to the existing water network is immediately near the outer wall of the unit. Price to include all the required fittings for functional ablution unit Price per one ablution. | LS | 1 |  | 0
7.5.24 | Design and built sewerage system with connections. The connection to the existing sewerage network is immediately near the outer wall of the unit. Price to include all the required fitting for functional ablution unit. For more details, refer to the technical specification. Price per one ablution. | LS | 1 |  | 0
7.5.25 | Closing the facade holes after removing the old sewerage pipes (the old network lies on the floor while the new one will lie under the floor, so the penetration into the facade will not be in the same place). The holes are to be closed nicely, to rece same surface as other part of the building. | EA | 1 |  | 0
7.5.26 | Provide and install single phase single sockets suitable for toilets/IP65/with cover, complete with required fittings 16A, 220V. Price is to include all the cabling provision and installation PPY 3x2,5mm², with the required fittings. Cables to be covered with PVC trunking. | EA | 3 |  | 0
7.5.27 | Provide and install surface mounted LED lights for toilets, IP65, water resistant, 1x40W (dim 30x120cm). Price is to include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC trunking. | EA | 2 |  | 0
7.5.28 | Provide and install surface mounted LED lights for toilets, IP65, water resistant, 1x18W (dim 10x60cm). Price is to include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC piping. | EA | 3 |  | 0
7.5.29 | Provide and install moving sensors for ablution units lights 360º, surface mounted with all required cabling/accessories for functional sensor. | EA | 4 |  | 0
7.5.30 | Provide and install new radiator dim 100/60cm in existing heating network, previously the old one to be dismantled. New radiator is to be equipped with thermo-head regulator. In the price to be calculated painting of existing heating pipes inside ablution unit with white color, heat resistant. | EA | 1 |  | 0
Ablution marked "B"
7.5.31 | Demolition of the complete partition walls and sanitary equipments , shower toilet and two washing base complete with old water and sewerage network. Debris to be transported to the city dump site. Prior to transportation clearance for the items to be taken from the EULEX Representative. Room will be used as kitchen | LS | 1 |  | 0
7.5.32 | Provide with material and install cover for remained sewerage pipe ᴓ100mm. Cover is to be done from prepainted flat metal sheet t-0.55mm, with under construction of steel profiles 20x20x2mm which are to be treated with antirust paint in two layers (see detail 3-3) | m' | 3 |  | 0
7.5.33 | Provide material and paint walls and ceiling initially with primer and then with acrylic enamel paint 2x. Paint characteristics: semi-gloss coating, eco-friendly, thinning with water. Paint is to be applied by spraying. Previously the surface is to be cleaned of dust and any debris. Painted wall should be washable. | m2 | 32 |  | 0
7.5.34 | Provide and install surface mounted LED lights for toilets, IP65, water resistant, 1x40W (dim 30x120cm). Price is to include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC trunking. | EA | 1 |  | 0
7.5.35 | Provide and install single phase sockets suitable for toilets/IP65/with cover, complete with required fittings 16A, 220V. Price is to include all the cabling provision and installation PPY 3x2,5mm², with the required fittings. Cabling is to be covered with PVC piping. | EA | 4 |  | 0
7.5.36 | Provide and install kitchen sink -stainless still with cabinet, complete with proper tap for cold and hot water. Cabinet is to be from plywood, white color. Bench top to be plastified and waterproof. In the price to be calculated all accessories for sink connection to the existing cold/hot water and sewerage system . Dim 120x60x90 | EA | 1 |  | 0
7.5.37 | Provide and install kitchen cabinet from white plywood, with upper working bench top from waterproof plasticized material. Dim 120x60x90 | EA | 1 |  | 0
7.5.38 | Provide and install new radiator dim 60/60cm in existing heating network, previously the old one to be dismantled. New radiator is to be equipped with thermo-head regulator. In the price to be calculated painting of existing heating pipes inside ablution unit with white color, heat resistant. | EA | 1 |  | 0
Ablution marked "C" & "D"
7.5.39 | Provide material and paint walls and ceiling initially with primer and then with acrylic enamel paint 2x. Paint characteristics: semi-gloss coating, eco-friendly, thinning with water. Paint is to be applied by spraying. Previously the surface is to be cleaned of dust/rust and any holes to be repaired. As well all equipment, windows, ACs, etc., are to be properly protected prior painting. Painted wall should be washable. | m2 | 86 |  | 0
7.5.40 | Provide and install surface mounted LED lights for toilets, IP65, water resistant, 1x40W (dim 30x120cm). Price is to include dismantling of old one and necessary cabling to adjust connection of new lights. | EA | 3 |  | 0
7.5.41 | Provide and install surface mounted LED lights for toilets, IP65, water resistant, 1x18W (dim 10x60cm). Price is to include dismantling of old one and necessary cabling to adjust connection of new lights. | EA | 3 |  | 0
7.5.42 | Provide and install moving sensors for ablution units lights 360º, surface mounted with all required accessories and necessary cabling for functional sensor . Cabling is to be covered with proper PVC piping. | EA | 5 |  | 0
7.5.43 | Provide and install single phase single sockets suitable for toilets/IP65/with cover, complete with required fittings 16A, 220V for existing washing machine.. Price is to include all the cabling provision and installation PPY 3x2,5mm², with the required fittings. Cables to be covered with PVC piping. | Ea | 1 |  | 0
7.5.44 | Provide and install new radiator in existing heating network, previously the old one to be dismantled. New radiators are to be equipped with thermo-head regulator. In the price to be calculated painting of existing heating pipes inside ablution unit with white color, heat resistant
| Ab.Unit #D- Dim 100x60cm |  | 1 |  | 0
| Ab.Unit #C- Dim 60x60cm |  | 1 |  | 0
7.6 | Painting and lightings improvements of the corridors in R1;R2;R3;Rn and O1 Ground & First Floor
Painting works
7.6.1 | Provide material and paint walls and ceiling of corridors initially with primer and then with acrylic enamel paint 2x. Paint characteristics: semi-gloss coating, eco-friendly, thinning with water. Paint is to be applied by spraying. Previously the surface is to be cleaned of dust/rust and any holes to be repaired. after cleaning, rusted area to be treated with anti-rust paint. As well all equipment, windows, etc., are to be properly protected prior painting. Painted wall should be washable. | m2 | 360 |  | 0
Improvement of the lighting in corridors
7.6.2 | Provide and install surface mounted LED lights 1x40W (dim 30x120cm). Price is to include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm² . Cabling is to be covered with proper PVC piping | EA | 52 |  | 0
7.6.3 | Provide and install surface mounted LED lights for Armstrong ceiling 1x40W (dim 60x60cm). Prior the old lights are to be dismantled. Price is to include also provision and installation of the required cabling for functional lights - Cable type PPY 3x1,5mm²as needed. Cabling is to be covered with proper PVC piping | EA | 13 |  | 0
7.6.4 | Provide and install moving sensors for ablution units lights 360º, surface mounted with all required accessories and necessary cabling for functional sensor . Cabling is to be covered with proper PVC piping. | EA | 27 |  | 0
7.7 | Painting of emergency stairs in all Residential Blocks-Dwg. A07 & A08
7.7.1 | R1; R2; R3: Provide material and paint the emergency metal stairs, treads, landing and complete steel structures with base paint 1x and final oil based paint 2x. Surface of painting need to be flat and uniformly. Prior painting , cleaning of dust/rust is to be done. Paint is to be applied by spraying. As well facade, windows, ACs,el. panels, are to be properly protected prior painting. In the price to be included use of proper ladders/scaffolding. Price per 1(one) set of stairs | LS | 3 |  | 0
7.7.2 | Rn&O1: Provide material and paint the emergency metal stairs, trades, landing and complete steel structures with base paint 1x and final oil based paint 2x. Surface of painting need to be flat and uniformly. Prior painting , cleaning of dust/rust is to be done. Paint is to be applied by spraying. As well facade, windows, ACs,el. panels, are to be properly protected prior painting. In the price to be included use of proper ladders/scaffolding. Price per1(one) set of stairs | LS | 1 |  | 0
|  |  |  | Total | 0

## Summary all
Summary ALL
ECM partial handover and relocation construction works
No | SUMMARY TABLE
1 | Dismantling and relocation works | 0
2 | Modification of ECM Main Entrance | 0
3 | SSD Block | 0
4 | FPU Commanders block | 0
5 | T walls - fence and infrastructure works | 0
6 | IT/Comms Works | 0
7 | FPU Ablution Units in residential blocks | 0
TOTAL |  | 0